## Slide 1: M2A Transmitter Service Training
Rev. 8-5-15

## Slide 2: Transmitter Specifications
Input power: 10-30 VDC, 0.160A
Housing: Explosion Proof Class I Div. 1 Group B,C, and D, epoxy-coated aluminum, NEMA 4X rating
Dimensions: 8.5” H x 5.2” W x 4.5” D
Weight: 4.5 lbs.
Temp Range: -40C to 75C
Rating: Indoor or outdoor locations Max humidity: 95% RH (non-condensing)
Relay contact rating: 5A @ 115/220V- Form C contacts
Signal output: 4-20 mA, 500 Ohms impedance max, and RS-485 Modbus

## Slide 3: Internal Description

## Slide 4: Calibration

## Slide 5: Non Intrusive Calibration
Using magnetic wand, place magnet over UP/YES Hall effect switch to engage Calibration Mode.
Rev. 3/15/06
<number>

## Slide 6: Non Intrusive Calibration
When Calib? YES/NO is displayed, touch magnet to glass where UP/YES Hall effect switch is located.
Rev. 3/15/06
<number>

## Slide 7: Non Intrusive Calibration
Gas type will be displayed.
Assemble calibration kit as needed.
Rev. 3/15/06
<number>

## Slide 8: Non Intrusive Calibration
When FreshAir Adjust is displayed, touch magnet to UP/YES Hall effect switch.
If you suspect that there may be gas in the atmosphere, use zero air to set FreshAir reading.
Rev. 3/15/06
<number>

## Slide 9: Non Intrusive Calibration
M2A will adjust to fresh air values.
Rev. 3/15/06
<number>

## Slide 10: Non Intrusive Calibration
PASS will be displayed if zero is successful.
If unable to set to fresh air values, FAIL will be displayed.
Replace sensor then perform zero again.
Rev. 3/15/06
<number>

## Slide 11: Non Intrusive Calibration
Once FreshAir adjustment is completed, new value will be saved in memory.
Rev. 3/15/06
<number>

## Slide 12: Non Intrusive Calibration
Instrument will ask if you want to SPAN with Cal Gas.
Place magnet over UP/YES Hall effect switch.
Rev. 3/15/06
<number>

## Slide 13: Non Intrusive Calibration
M2A will indicate SPAN Gas.
Rev. 3/15/06
<number>

## Slide 14: Non Intrusive Calibration
Attach span gas cylinder to regulator.
Attach calibration cup to sensor and turn on regulator.
Rev. 3/15/06
<number>

## Slide 15: Non Intrusive Calibration
Allow gas reading to stabilize.
Maximum of 2 minutes.
Rev. 3/15/06
<number>

## Slide 16: Non Intrusive Calibration
Place magnet over UP/YES Hall effect switch and adjust span for maximum value to determine headroom of the sensor.
Rev. 3/15/06
<number>

## Slide 17: Non Intrusive Calibration
Place the magnet over the DOWN/NO Hall effect switch and adjust reading to calibration point. Then place magnet over ENTER Hall effect switch to set.
Rev. 3/15/06
<number>

## Slide 18: Non Intrusive Calibration
Once completed, new SPAN value will be saved in memory.
Remove calibration cup from sensor and turn off regulator.
Rev. 3/15/06
<number>

## Slide 19: Non Intrusive Calibration
M2A will allow sensor reading to stabilize and return to normal operation.
Rev. 3/15/06
<number>

## Slide 20: Sensor with Cal Adapter
IR sensor mounted on ceiling with remote calibration adapter and tubing installed.
Rev. 3/15/06
<number>

## Slide 21: Remote Cal Tubing
Remote calibration tubing provides a convenient way to apply calibration gas to the sensor.
Rev. 3/15/06
<number>

## Slide 22: Remote Cal Adapter
For sensors using a remote calibration adapter, it may be required to use a higher flow regulator, especially in high ventilation areas.
IR sensor with remote calibration adapter shown.
Rev. 3/15/06
<number>

## Slide 23: Remote Cal Adapter
Remote calibration adapter for catalytic bead LEL sensor shown.
Rev. 3/15/06
<number>

## Slide 24: Configuration Mode

## Slide 25: Configuration Mode
Press the UP/YES and ENTER buttons to enter the CONFIG mode.
Rev. 3/15/06
<number>

## Slide 26: Configuration Mode
The Configuration Mode allows the user to change the M2A Transmitter’s parameters.
The Configuration Mode includes a 5 minute time out feature if a control button is not pressed for 5 minutes.

## Slide 27: Configuration Mode
Press the UP/YES button to continue.
Rev. 3/15/06
<number>

## Slide 28: Configuration Mode
Configuration Mode
  Alarm-1 (Set Point)
  Alarm-1 (activation-Increase/Decrease)
  Alarm-1 (relay action N.DE-EN or N. EN)
  Alarm-1 (relay reset LATCH or SELF-RST
  A1 OnDY (alarm On delay, 1 sec std.)
Rev. 3/15/06
<number>

## Slide 29: Configuration Mode
  ALARM-2 (level)
  ALARM-2 (activation Increase/Decrease)
  ALARM-2 (relay action N. DE-EN / N. EN)
  ALARM-2 (relay reset, LATCH/SELF-RST)
  A2 OnDy (alarm 2 On delay, 1 sec. std.)
  ZeroSupp (0.5% for O2, 2% of scale for others
  Filter (5 sec.) reduces jumpy or noisy signals
  CAL Time (15 minutes) adjustable from 5 minutes to 30 minutes.
Rev. 3/15/06
<number>

## Slide 30: Gas Type
While in normal operation, press and HOLD the YES and DOWN/NO buttons for five seconds.
Release when display shows Select Gas Type?
Rev. 3/15/06
<number>

## Slide 31: Gas Type
This is dependent on the type of M2A that you have.
Press the UP/YES button to select gas type.
Once gas type is selected M2A will ask if you want to save change.
Press UP/YES button to save changes.
Rev. 3/15/06
<number>

## Slide 32: Detector Type
Detector Head Input Type | Description
H2S | An H2S detector is connected to the M2A Transmitter with 2 wires using the TOX + and - terminals from the detector/transmitter terminal strips.
CO | A CO detector is connected to the M2A Transmitter with 2 wires using the TOX + and - terminals from the detector/transmitter terminal strips.
OXYGEN | An oxygen detector is connected to the M2A Transmitter with 2 wires using the OXY + and - terminals from the detector/transmitter terminal strips.
LEL | An LEL detector head is wired to the M2A Transmitter with 4 wires using the LEL BLK, GRN, WHT, and RED terminals.

## Slide 33: 4-20 mA Output Operation
  If you enter calibration mode the output is fixed at 3.5 mA or 17.4 mA for O2.
  If the Transmitters input power decreases below 9.5 Volts and is in low power alarm. Output is fixed below 2.4 mA until power alarm clears.
  If the Transmitter goes into fail condition after 30 second delay. Output is fixed below. 2.4 mA until fault alarm clears.
Rev. 3/15/06
<number>

## Slide 34: Trouble Shooting
Rev. 3/15/06
<number>

## Slide 35: Questions?
07/29/26
<number>